# 2022 RCM Limit Advice WEM Report Version 1.4 Public 7 July 2023

Western Power

363 Wellington Street

Perth WA 6000

GPO Box L921 Perth WA 6842

Electricity Networks Corporation

ABN 18 540 492 861

WEMLimitAdvice@westernpower.com.au

westernpower.com.au

ELECTRICITY INDUSTRY ACT 2004

ELECTRICITY INDUSTRY

(WHOLESALE ELECTRICITY MARKET)

REGULATIONS 2004

WHOLESALE ELECTRICITY MARKET RULES

Authorisation

|  | Title | Name | Date |
| --- | --- | --- | --- |
| Approver: | Transmission Grid Strategy & Planning Manager | Daniel Cassidy | 7 Jul 2023 |

Version Release History

| Version | Effective Date | Summary of Changes |
| --- | --- | --- |
| 1.0 | 15 Jul 2022 | 2022 RCM Limit Advice – original version |
| 1.1 | 11 Nov 2022 | Some minor changes to thermal ratings |
| 1.2 | 20 Apr 2023 | Include recently committed future block loads and changes to some line ratings |
| 1.3 | 15 Jun 2023 | Include some line upgrades in Kwinana load area, new special protection schemes and changes to some T line ratings |
| 1.4 | 7 Jul 2023 | Changes to new special protection schemes, NOP and add missing line ratings |

DISCLAIMER

Western Power provides this Limit Advice and associated information in good faith and in the performance of its functions conferred under rules 4.4B.3 and 4.4B. the Wholesale Electricity Market Rules. Western Power has used reasonable endeavours to ensure that this Limit Advice and information is complete, current and accurate at the time it is provided to AEMO. Western Power is not liable for any acts, errors or omissions, or for any results obtained by any party from the use of this information, generally and in accordance with its statutory immunity under section 126 of the Electricity Industry Act 2004 (WA).”

Contents

Abbreviations	1

1.	Purpose	2

2.	Provided information	2

2.1	Estimated SWIS configuration	2

2.2	Estimated proportion of the peak demand	2

2.3	RCM thermal network limit	3

2.4	Normally open points (NOP) in summer 2025	4

2.5	Facilities subject to NCS or NCESS	4

# Abbreviations

The following table provides a list of abbreviations and acronyms used throughout this document. Defined terms are identified in this document by capitals.

| Term | Definition |
| --- | --- |
| APJ-PNJ 81 | Alcoa Pinjarra-Pinjarra 132kV line |  |
| JDP-WNO 81 | Joondalup-Wanneroo 132kV line |  |
| KEM-MRR 81 or 82 | Kemerton-Marriot Road 132kV #1 & #2 lines |  |
| KW-MED/CC 81 | Kwinana terminal to the T point of Kwinana-Medina-Cockburn Cement 132kV T line |  |
| MED-KW/CC 81 | Medina substation to the T point of Kwinana-Medina-Cockburn Cement 132kV T line |  |
| MSR-OFE/WM 81 | Mason Road substation to the T point of Mason Road-Office Road-Western Mining 132kV T line |  |
| NBT T2 transformer | Neerabup 330/132kV T2 transformer |  |
| NCESS | Non-Co-optimised Essential System Services |  |
| NCS | Network Control Services |  |
| PIC-MRR 81 | Picton-Marriot Road 132kV line |  |
| PNJ-MH 81 | Pinjarra-Mandurah 132kV line |  |
| PNJ-MSS-CT 81 | Pinjarra-Meadow Spring-Canninton Terminal 132kV line |  |
| PJR-YP 81 | Pinjar-Yanchep 132kV line |  |
| RCM | Reserve Capacity Mechanism |  |
| SWIS | South West Interconnected System |  |
| WGP-APJ-SNR | Wagerup-Alcoa Pinjarra-Southern River 132kV line |  |
| WEM | Wholesale Electricity Market |  |
| WM-AFM/RO 81 | Western Mining substation to the T point of Western Mining-Australian Fused Materials-Rockingham 132kV T line |  |
| WM-OFE/MSR | Western Mining substation to the T point of Mason Road-Office Road-Western Mining 132kV T line |  |

# Purpose

This Limit Advice is to provide AEMO with the requested information in accordance with Western Power’s obligation, as a Network Operator, specified in clauses 4.4B.3 and 4.4B.5 of the WEM Rules.

# Provided information

All the requested information are in the following sub sections or referenced attachments.

## Estimated SWIS configuration

The estimated configuration of the SWIS during summer 2025 peak, without the recently approved projects and the proposed connection points of the Facilities notified in AEMO’s Expression of Interest spreadsheet, is available from the SWIS PowerFactory Base Model Version 202110v1, uploaded to the “SWIS Powerfactory Model Upload” directory in AEMO’s portal on 22/11/2021.

The proposed connection points of the notified Facilities for the RCM constraint equation development purposes are provided under the “Substation for proposed connection” column of the “2022 RCM – EOI V0 published” spreadsheet uploaded to the “2022 Capacity Cycle” directory in AEMO’s portal on 23 Nov 2022.

The special protection/control schemes applicable to the RCM constraint equation development, but not limited to, are notified under the “Include in limit & constraint equation” column of the “Existing Special Protection Scheme Register (Ver 6C)” file uploaded to the “SWIS Special Protection Schemes” directory in AEMO’s portal on 8 Jul 2022.

In addition, Western Power will implement additional Special Protection Schemes in the form of “manual intervention processes”. A “manual intervention process” means that the Western Power control room will perform the specified action, post-contingency, but before overloaded equipment is damaged (e.g. by relying on short-term overload capacity). AEMO can assume that the “manual intervention process” is “in service” and dispatch generation accordingly, unless they have been specifically notified by Western Power that it is “out of service”, in a manner similar to an outage of a notification list item, unless otherwise agreed (e.g. by phone or SCADA signal, and then referenced in an associated planned or forced outage submission). The following operational manual interventions, for only N-1 system, will be implemented before 1st October 2024:

- Open the 132kV circuit breaker at WNO of JDP-WNO 81 line when PJR-YP 81 is overloaded while NBT T2 transformer is out of service; and

- Open the 132kV circuit breaker at MRR of PIC-MRR 81 line when KEM-MRR 81 or 82 line is overloaded.

- Open the 132kV circuit breaker at WGP of WGP-APJ-SNR 81 line when APJ-PNJ 81, PNJ-MSS-CT 81 or PNJ-MH 81 line is overloaded

## Estimated proportion of the peak demand

The estimated proportion of the SWIS peak demand during summer 2025 at each Electrical Location is in the “2022 RCM – peak demand and block loads V3 published” file uploaded to the “2022 Capacity Cycle” directory in AEMO’s portal on 5 May 2023. It includes a new load with an estimated peak demand > 10MW and with a forecast in service date between summer 2022 and summer 2025, details in the below table. There are no existing loads having a change in demand of more than 10MW between summer 2022 and summer 2025.

Table 2.1:	New load with estimated peak demand > 10MW

| # | Description | Estimated peak demand in 2022 RCM (MW) | Estimated peak demand in previous RCM year (MW) | New/Existing load | Substation | Forecast in service date |
| --- | --- | --- | --- | --- | --- | --- |
| 1 | Block load 24 | 29 | NA | New | MRN (Mason Rd North) | Oct 2023 |
| 2 | Block load 36 | 10 | NA | New | WHT (Whiteman Park) | Feb 2024 |
| 3 | Block load 38 | 15 | NA | New | BTN (Bridgetown) | Jun 2023 |

## RCM thermal network limit

The following information has been included the “2022 RCM -thermal ratings V5 published” file uploaded to the “2022 Capacity Cycle” directory in AEMO’s portal on 7 July 2023:

Thermal ratings of all applicable lines and transformers assuming an ambient temperature of 41 degrees Celsius;

Transmission Network assets scheduled to be commissioned or retired. Note that none of them are associated with AEMO’s list of Facilities ceasing operation permanently; and

Proposed changes to the SWIS to facilitate the connection of new Facilities notified in AEMO’s Expression of Interest spreadsheet.

- It also includes the RCM ratings of the following future line upgrades (to be completed before 1st October 2024):

| 132 kV line section | RCM rating (A) |
| --- | --- |
| KW-MED/CC | 1440 |
| WM-OFE/MSR | 1053 |
| MSR-OFE/WM | 1053 |
| MED-KW/CC | 1053 |
| WM-AFM/RO | 1053 |

## Normally open points (NOP) in summer 2025

Table 2.2 lists out the expected NOP under N-0 system during high load periods in summer 2025.

Table 2.2: Expected NOP in summer 2025

| # | NOP |
| --- | --- |
| 1 | BEL end of BEL-EP-NT 81 line |
| 2 | PIC end of PIC-PNJ-BSN-KEM 81 line |
| 3 | NGN & NGS ends of NGN-NGS-WAG 71 line |
| 4 | KEL end of CUN-KEL |
| 5 | SX end of YLN-SX |
| 6 | 132kV end of KW BTT1 330/132kV transformer |
| 7 | HAY end of HAY-MIL 81 cable |
| 8 | MLA bus section 804 at MLA 132kV busbar |
| 9 | 132kV end of KEM T1 330/132kV transformer |
| 10 | 22kV ends of NOR T1, T2 & T3 transformer |
| 11 | 22kV isolator 505.4 at WGP 22kV bus |

In addition to the above NOP, the NBT T2 transformer can be taken out of service daily when required.

## Facilities subject to NCS or NCESS

There are no facilities required to be in service during summer 2025 to provide NCS, NCESS or equivalent service.

Following a single contingency after N-0 system