## Version history
Special schemes applicable to 2024 RCM
Version History | Date | Details
7.4 | 2024-09-20 | Align with Special Protection Scheme Register V7.4
7.4a | 2024-10-15 | Incl MDP in 220kV inter-trip

## Scheme
Special schemes applicable to 2024 RCM
# | Name | Contingency/Trigger | Scheme response/ Outcome
1 | MARNET | ENT-YDT 91 is part of contingency | intertrip WDW-ENT 91 line. Run back KRA to 10.0MW. Disconnect WARRADARGE_WF1
|  | NBT-YDT 91 is part of contingency | intertrip ENT-YDT 91 & WDW-ENT 91 line. Run back KRA to 10.0MW. Disconnect YANDIN_WF1 and WARRADARGE_WF1
|  | NBT-NT 91 is part of contingency | intertrip NBT-YDT 91, ENT-YDT 91 & WDW-ENT 91 line. Run back KRA to 10.0MW. Disconnect YANDIN_WF1 and WARRADARGE_WF1
|  | ENT-TST 91 is part of contingency | runback KRA to 10.0MW
2 | 220kV inter-trip | CGT-YLN-WKT X1 | Disconnect CGW. Island EGF
|  | MRT-CGT X1 | Disconnect CGW. Intertrip CGT-YLN-WKT line. Island EGF
|  | KDN-MRT X1 | Disconnect MDP, CGW & MRS. Intertrip MRT-CGT & CGT-YLN-WKT lines. Island EGF
|  | MU-NGS-KDN X1 | Disconnect MDP, CGW & MRS. Intertrip MRT-CGT & CGT-YLN-WKT lines. Island EGF
3 | BGM runback | PMT-WLT 91 | Run back BGM to 35MW
4 | MRT-CNS-NOR decouple | MRT-CNS-NOR 81 overload (measured at MRT & NOR taking into account losses on NOR-CNS/MRT section) | Open MRT CB of MRT-CNS-NOR 81 line
5 | APJ | SNR-APJ/WGP overload (measured in to SNR) | Run back ALINTA_PNJ_U1 to 83.0MW first, if overload remains, disconnect this unit.
6 | WWF runback | HBK-MUC 81 overloaded (measured at both MUC and HBK ends) | Disconnect TESLA_GERALDTON_G1 then runback Alinta_WWF, if overload remains, disconnect Alinta_WWF
MOR-MUC 81 is overloaded (measured at MOR of MOR to MUC flow)
ENB-TS 81 is overloaded (measured at TS of TS to ENB flow)
MOR-TS 81 is overloaded (measured at both TS and MOR ends)
MGA-TS 81 is overloaded (measured at MGA of MGA to TS flow)
MGA-MBA 81 is overloaded (measured at MGA of MGA to MBA flow)
TS-MBA 81 is overloaded (measured at MBA of MBA to TS flow)
7 | TS bus coupler | TS806 overload (measured at TS of MGA to TS and MBA to TS flow) & GRSF ≥ 10MW | Run back GRSF first, if overload remains, disconnect this unit.
8 | NT 132kV bus coupler | A forced outage of one of NT 330kV transformers | NT 132kV bus couplers will close to re-mesh NT 132kV buses
9 | PIC-MRR intertrip | PIC-MRR overload (measured at PIC of PIC to MRR flow) | Disconnect MRR 526, 512 & 531 feeders
10 | PJR-YP manual intertrip | PJR-YP 81 overloaded (measured at PJR of PJR to YP flow) & NBT T2 oos under a defined system configuration | Manually take JDP-WNO 81 out of service
11 | KEM-MRR 81/82 manual intertrip | KEM-MRR 81 or 82 overloaded (measured at KEM of KEM to MRR flow) under a defined system configuration | Manually take MRR-PIC 81 out of service
12 | WGP manual intertrip | APJ-PNJ 81 overloaded (measured at APJ of APJ to PNJ flow) under a defined system configuration | Open WGP circuit breaker of WGP-APJ-SNR 81 line
CT-MSS-PNJ 81 overloaded (measured at PNJ of PNJ to T point flow) under a defined system configuration
PNJ-MH 81 overloaded (measured at PNJ of PNJ to MH flow) under a defined system configuration
13 | MUL-PBY manual intertrip | NT-BCT 81 overloaded (measured at NT of NT to BCT flow) under a defined system configuration | Take MUL-PBY 81 line out of service