## Authorisation
2026 RCM - Peak demand and block loads
Version # | Date | Summary of change
0 | 2026-05-22 | Original version
1 | 2026-08-11 | Update Block Load 30
Authorisation
| Date | Title | Name
Approver | 2026-08-11 | A/Transmission System Planning Manager | A Muthuveerappan
VOLT# | ID39-644322706-331324

## Proposed Electrical Location
Table 1 1. The estimated zone substation load (%) and Block loads (MW) are based on information from the applicable SWIS Base Model for the relevant reserve capacity cycle. 2. Connection points expected to export MW into the grid during the system coincident peak demand are excluded.
Capacity Year (3rd year of a Reserve Capacity Cycle) | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34
Estimated peak demand from WEM ESOO
Table 2 1. The demand at the following Electrical Locations are given as percentages, up to 2 decimal places. 2. Where an Electrical Location has one or more block loads, as specified in Table 3, the demand in Table 2 is the net demand at the Electrical Location, that is, the total load demand at the Electrical Location minus the total load demand of the block loads at the Electrical Location. 3. The estimated proportion of peak demand at an Electrical Connection is the net demand at that location divided by the sum of the demand at all Electrical Locations in the SWIS (=Western Power peak demand forecast for SWIS in summer) 4. Variation in estimated peak demand of the existing electrical connections and block loads is due to distribution load transfer, recent historical data, PV penetration, different load growth rate, etc. | bar: 2024-25
Electrical Location | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34
A - Arkana | 2024-25: 1.084%; 2025-26: 1.122%; 2026-27: 1.146%; 2027-28: 1.259%; 2028-29: 1.214%
ALB - Albany | 2024-25: 0.8206%; 2025-26: 0.7971%; 2026-27: 0.8279%; 2027-28: 0.7999%; 2028-29: 0.8648%
AMT - Amherst | 2024-25: 1.708%; 2025-26: 1.568%; 2026-27: 1.619%; 2027-28: 1.585%; 2028-29: 1.358%
APM - Australian Paper Mills | 2024-25: 0.5871%; 2025-26: 0.6139%; 2026-27: 0.6398%; 2027-28: 0.6154%; 2028-29: 0.7938%
BCH - Beechboro | 2024-25: 1.484%; 2025-26: 1.594%; 2026-27: 1.641%; 2027-28: 1.63%; 2028-29: 1.778%
BCT - Balcatta | 2024-25: 0.2959%; 2025-26: 0.2693%; 2026-27: 0.2918%; 2027-28: 0.386%; 2028-29: 0.4142%
BEL - Belmont | 2024-25: 0.9478%; 2025-26: 0.838%; 2026-27: 0.8603%; 2027-28: 1.008%; 2028-29: 0.8852%
BIB - Bibra Lake | 2024-25: 1.239%; 2025-26: 1.241%; 2026-27: 1.277%; 2027-28: 1.321%; 2028-29: 1.336%
BKF - Black Flag | 2024-25: 0.7998%; 2025-26: 0.8423%; 2026-27: 0.8819%; 2027-28: 0.6219%; 2028-29: 0.5116%
BLD - Boulder | 2024-25: 0.6264%; 2025-26: 0.4632%; 2026-27: 0.4993%; 2027-28: 0.4289%; 2028-29: 0.5116%
BNP - Beenup | 2024-25: 0.1479%; 2025-26: 0.14%; 2026-27: 0.1708%; 2027-28: 0.1137%; 2028-29: 0.1401%
BSN - Busselton | 2024-25: 0.957%; 2025-26: 1.336%; 2026-27: 0.8365%; 2027-28: 1.212%; 2028-29: 1.411%
BTN - Bridgetown | 2024-25: 0.5871%; 2025-26: 0.642%; 2026-27: 0.6852%; 2027-28: 0.1287%; 2028-29: 0.2375%
BTY - Bentley | 2024-25: 0.846%; 2025-26: 0.8725%; 2026-27: 0.9035%; 2027-28: 0.8792%; 2028-29: 0.8953%
BUH - Bunbury Harbour | 2024-25: 1.447%; 2025-26: 1.4%; 2026-27: 1.431%; 2027-28: 1.432%; 2028-29: 1.48%
BYF - Byford | 2024-25: 1.78%; 2025-26: 1.915%; 2026-27: 1.993%; 2027-28: 1.81%; 2028-29: 1.764%
CAP - Capel | 2024-25: 0.4739%; 2025-26: 0.4869%; 2026-27: 0.5144%; 2027-28: 0.4267%; 2028-29: 0.4466%
CAR - Carrabin | 2024-25: 0.006935%; 2025-26: 0.006463%; 2026-27: 0.03458%; 2027-28: 0%; 2028-29: 0.0203%
CC - Cockburn Cement | 2024-25: 0.7559%; 2025-26: 1.049%; 2026-27: 1.079%; 2027-28: 1.042%; 2028-29: 1.194%
CK - Cook Street | 2024-25: 1.026%; 2025-26: 0.9435%; 2026-27: 0.4971%; 2027-28: 1.004%; 2028-29: 1.498%
CKN - Clarkson | 2024-25: 1.579%; 2025-26: 1.579%; 2026-27: 1.643%; 2027-28: 1.535%; 2028-29: 1.49%
CL - Clarence St | 2024-25: 0.6704%; 2025-26: 0.5967%; 2026-27: 0.6268%; 2027-28: 0.6669%; 2028-29: 0.5948%
CO - Collie | 2024-25: 0.289%; 2025-26: 0.3124%; 2026-27: 0.3415%; 2027-28: 0.3131%; 2028-29: 0.2984%
COL - Collier | 2024-25: 0.8992%; 2025-26: 0.9392%; 2026-27: 0.9684%; 2027-28: 0.8706%; 2028-29: 1.127%
CPN - Chapman | 2024-25: 0.2728%; 2025-26: 0.2779%; 2026-27: 0.3069%; 2027-28: 0.2959%; 2028-29: 0.2639%
CTE - Cottesloe 132kV | 2024-25: 1.075%; 2025-26: 0.9672%; 2026-27: 0.9921%; 2027-28: 1.042%; 2028-29: 0.9603%
CUN - Cunderdin | 2024-25: 0.1364%; 2025-26: 0.1228%; 2026-27: 0.1491%; 2027-28: 0.1673%; 2028-29: 0.1847%
CVE - Canning Vale | 2024-25: 1.16%; 2025-26: 1.068%; 2026-27: 1.089%; 2027-28: 1.186%; 2028-29: 1.338%
D - Darlington | 2024-25: 0.5016%; 2025-26: 0.4739%; 2026-27: 0.5036%; 2027-28: 0.4996%; 2028-29: 0.4304%
E - Edmund Street | 2024-25: 0.5178%; 2025-26: 0.4761%; 2026-27: 0.4971%; 2027-28: 0.5554%; 2028-29: 0.4913%
ENB - Eneabba | 2024-25: 0.1595%; 2025-26: 0.1486%; 2026-27: 0.1772%; 2027-28: 0.163%; 2028-29: 0.3593%
FFD - Forrestfield | 2024-25: 0.6912%; 2025-26: 0.5859%; 2026-27: 0.5966%; 2027-28: 0.7034%; 2028-29: 0.7248%
G - Gosnells | 2024-25: 1.114%; 2025-26: 1.374%; 2026-27: 1.394%; 2027-28: 1.503%; 2028-29: 1.372%
GTN - Geraldton | 2024-25: 0.6519%; 2025-26: 0.6139%; 2026-27: 0.6506%; 2027-28: 0.6369%; 2028-29: 0.674%
H - Hadfields | 2024-25: 1.07%; 2025-26: 1.103%; 2026-27: 1.12%; 2027-28: 1.209%; 2028-29: 1.104%
HAY - Hay Street | 2024-25: 1.068%; 2025-26: 1.215%; 2026-27: 0.6312%; 2027-28: 1.094%; 2028-29: 0.8445%
HBK - Henley Brook | 2024-25: 1.436%; 2025-26: 1.736%; 2026-27: 1.848%; 2027-28: 1.218%; 2028-29: 1.435%
HZM - Hazelmere | 2024-25: 0.5733%; 2025-26: 0.5407%; 2026-27: 0.5793%; 2027-28: 0.5404%; 2028-29: 0.538%
JDP - Joondalup | 2024-25: 1.114%; 2025-26: 1.135%; 2026-27: 1.167%; 2027-28: 1.083%; 2028-29: 0.9217%
JTE - Joel Terrace 132kV | 2024-25: 1.258%; 2025-26: 1.183%; 2026-27: 1.21%; 2027-28: 1.252%; 2028-29: 1.242%
K - Kalamunda | 2024-25: 0.6981%; 2025-26: 0.7604%; 2026-27: 0.7846%; 2027-28: 0.8363%; 2028-29: 0.6618%
KAT - Katanning | 2024-25: 0.2543%; 2025-26: 0.2348%; 2026-27: 0.2615%; 2027-28: 0.2402%; 2028-29: 0.2619%
KDL - Kewdale | 2024-25: 0.5987%; 2025-26: 0.6118%; 2026-27: 0.6376%; 2027-28: 0.6369%; 2028-29: 0.4852%
KDN - Kondinin | 2024-25: 0.1641%; 2025-26: 0.1529%; 2026-27: 0.1794%; 2027-28: 0.1694%; 2028-29: 0.1543%
KEL - Kellerberrin | 2024-25: 0.06472%; 2025-26: 0.06032%; 2026-27: 0.08862%; 2027-28: 0.06219%; 2028-29: 0.07106%
KOJ - Kojonup | 2024-25: 0.05086%; 2025-26: 0.04524%; 2026-27: 0.07349%; 2027-28: 0.05147%; 2028-29: 0.05887%
LDE - Landsdale | 2024-25: 1.898%; 2025-26: 1.775%; 2026-27: 1.816%; 2027-28: 1.823%; 2028-29: 1.852%
MA - Manning Street | 2024-25: 0.7212%; 2025-26: 0.7303%; 2026-27: 0.7608%; 2027-28: 0.7806%; 2028-29: 0.7979%
MBR - Mount Barker | 2024-25: 0.1433%; 2025-26: 0.1422%; 2026-27: 0.1708%; 2027-28: 0.1372%; 2028-29: 0.1076%
MCE - Medical Centre 132kV | 2024-25: 1.052%; 2025-26: 0.9823%; 2026-27: 1.016%; 2027-28: 1.04%; 2028-29: 0.9562%
MDN - Maddington | 2024-25: 0.4762%; 2025-26: 0.5235%; 2026-27: 0.549%; 2027-28: 0.549%; 2028-29: 0.5847%
MDY - Munday | 2024-25: 0.497%; 2025-26: 0.4632%; 2026-27: 0.4907%; 2027-28: 0.371%; 2028-29: 0.5096%
MED - Medina | 2024-25: 1.357%; 2025-26: 1.398%; 2026-27: 1.459%; 2027-28: 1.447%; 2028-29: 1.338%
MER - Merredin | 2024-25: 0.1896%; 2025-26: 0.1788%; 2026-27: 0.2075%; 2027-28: 0.1844%; 2028-29: 0.2253%
MH - Mandurah | 2024-25: 1.678%; 2025-26: 1.762%; 2026-27: 1.794%; 2027-28: 1.456%; 2028-29: 1.541%
MIL - Milligan Street | 2024-25: 1.359%; 2025-26: 1.416%; 2026-27: 0.262%; 2027-28: 1.119%; 2028-29: 0.7962%
MJ - Midland Junction | 2024-25: 1.119%; 2025-26: 1.209%; 2026-27: 1.239%; 2027-28: 1.39%; 2028-29: 1.51%
MJP - Manjimup | 2024-25: 0.252%; 2025-26: 0.2887%; 2026-27: 0.3177%; 2027-28: 0.2959%; 2028-29: 0.2355%
MLG - Malaga | 2024-25: 0.8414%; 2025-26: 0.8294%; 2026-27: 0.3048%; 2027-28: 1.366%; 2028-29: 1.267%
MO - Morley | 2024-25: 1.153%; 2025-26: 1.217%; 2026-27: 1.249%; 2027-28: 1.327%; 2028-29: 1.289%
MOR - Moora | 2024-25: 0.2751%; 2025-26: 0.2844%; 2026-27: 0.1038%; 2027-28: 0.2916%; 2028-29: 0.3005%
MR - Margaret River | 2024-25: 0.2843%; 2025-26: 0.265%; 2026-27: 0.294%; 2027-28: 0.3259%; 2028-29: 0.337%
MRR - Marriott Road | 2024-25: 1.345%; 2025-26: 1.445%; 2026-27: 0.006485%; 2027-28: 0.3774%; 2028-29: 0.4791%
MSR - Mason Road | 2024-25: 0.7651%; 2025-26: 0.6269%; 2026-27: 0.2378%; 2027-28: 0.4932%; 2028-29: 0.5177%
MSS - Meadow Springs | 2024-25: 1.644%; 2025-26: 1.863%; 2026-27: 1.926%; 2027-28: 1.716%; 2028-29: 1.866%
MUC - Muchea | 2024-25: 0.6218%; 2025-26: 0.5838%; 2026-27: 0.616%; 2027-28: 0.6433%; 2028-29: 0.609%
MUL - Mullaloo | 2024-25: 1.119%; 2025-26: 0.9909%; 2026-27: 1.009%; 2027-28: 1.098%; 2028-29: 1.301%
MUR - Murdoch | 2024-25: 0.7605%; 2025-26: 0.7023%; 2026-27: 0.7284%; 2027-28: 0.7891%; 2028-29: 0.8019%
MYR - Myaree | 2024-25: 0.9894%; 2025-26: 0.9134%; 2026-27: 0.9403%; 2027-28: 0.9585%; 2028-29: 0.9846%
NB - North Beach | 2024-25: 1.331%; 2025-26: 1.303%; 2026-27: 1.347%; 2027-28: 1.218%; 2028-29: 1.273%
NGN - Narrogin | 2024-25: 0.3074%; 2025-26: 0.3081%; 2026-27: 0.3394%; 2027-28: 0.2938%; 2028-29: 0.2152%
NOR - Northam | 2024-25: 0.5224%; 2025-26: 0.5924%; 2026-27: 0.629%; 2027-28: 0.6755%; 2028-29: 0.3573%
NP - North Perth | 2024-25: 1.209%; 2025-26: 1.187%; 2026-27: 1.219%; 2027-28: 1.248%; 2028-29: 1.267%
OC - OConnor | 2024-25: 1.225%; 2025-26: 1.137%; 2026-27: 1.176%; 2027-28: 1.074%; 2028-29: 1.104%
OP - Osborne Park | 2024-25: 0.9663%; 2025-26: 0.8208%; 2026-27: 0.8387%; 2027-28: 0.9928%; 2028-29: 0.9136%
PBY - Padbury | 2024-25: 1.5%; 2025-26: 1.452%; 2026-27: 1.463%; 2027-28: 1.587%; 2028-29: 1.362%
PCY - Piccadilly St | 2024-25: 0.5756%; 2025-26: 0.5321%; 2026-27: 0.5533%; 2027-28: 0.5297%; 2028-29: 0.5786%
PIC - Picton | 2024-25: 0.92%; 2025-26: 0.6613%; 2026-27: 0.6809%; 2027-28: 0.8942%; 2028-29: 0.9603%
PNJ - Pinjarra | 2024-25: 0.4739%; 2025-26: 0.489%; 2026-27: 0.5339%; 2027-28: 0.7977%; 2028-29: 0.6882%
RAN - Rangeway | 2024-25: 0.5756%; 2025-26: 0.7023%; 2026-27: 0.7479%; 2027-28: 0.7977%; 2028-29: 0.672%
RGN22 - Regans 22kV | 2024-25: 0.1318%; 2025-26: 0.1653%; 2026-27: 0.1967%; 2027-28: 0.1673%; 2028-29: 0.136%
RGN33 - Regans 33kV | 2024-25: 0.1641%; 2025-26: 0.1739%; 2026-27: 0.2053%; 2027-28: 0.1887%; 2028-29: 0.1421%
RO - Rockingham | 2024-25: 1.348%; 2025-26: 1.094%; 2026-27: 1.096%; 2027-28: 1.192%; 2028-29: 1.271%
RTN - Riverton | 2024-25: 1.757%; 2025-26: 1.415%; 2026-27: 1.437%; 2027-28: 1.634%; 2028-29: 1.722%
RVE - Rivervale | 2024-25: 1.234%; 2025-26: 1.211%; 2026-27: 1.241%; 2027-28: 1.19%; 2028-29: 1.391%
SNR - Southern River | 2024-25: 1.919%; 2025-26: 2.034%; 2026-27: 2.123%; 2027-28: 1.984%; 2028-29: 2.191%
SPK - Shenton Park 132kV | 2024-25: 1.177%; 2025-26: 1.14%; 2026-27: 1.167%; 2027-28: 1.242%; 2028-29: 1.218%
SVY - Sawyers Valley 132kV | 2024-25: 0.5825%; 2025-26: 0.5838%; 2026-27: 0.4323%; 2027-28: 0.4139%; 2028-29: 0.4385%
SX - Southern Cross | 2024-25: 0.01156%; 2025-26: 0.03016%; 2026-27: 0.06052%; 2027-28: 0.0193%; 2028-29: 0.02233%
TS - Three Springs | 2024-25: 0.2127%; 2025-26: 0.1939%; 2026-27: 0.2248%; 2027-28: 0.1265%; 2028-29: 0.1563%
WAG - Wagin | 2024-25: 0.1017%; 2025-26: 0.1056%; 2026-27: 0.134%; 2027-28: 0.09864%; 2028-29: 0.1015%
WAI - Waikiki | 2024-25: 1.852%; 2025-26: 1.822%; 2026-27: 1.891%; 2027-28: 1.883%; 2028-29: 1.75%
WD - Wembley Downs | 2024-25: 0.8114%; 2025-26: 0.7497%; 2026-27: 0.7825%; 2027-28: 0.8492%; 2028-29: 0.8242%
WE - Welshpool | 2024-25: 1.26%; 2025-26: 1.329%; 2026-27: 1.347%; 2027-28: 1.465%; 2028-29: 1.324%
WGA - Wangara | 2024-25: 0.3837%; 2025-26: 0.4007%; 2026-27: 0.4323%; 2027-28: 0.5061%; 2028-29: 0.6375%
WGP - Wagerup | 2024-25: 0.3976%; 2025-26: 0.3662%; 2026-27: 0.3977%; 2027-28: 0.3838%; 2028-29: 0.3898%
WKT11 - West Kalgoorlie 11 kV | 2024-25: 0.1503%; 2025-26: 0.1551%; 2026-27: 0.1837%; 2027-28: 0.178%; 2028-29: 0.1662%
WKT33 - West Kalgoorlie 33 kV | 2024-25: 0.5109%; 2025-26: 0.5192%; 2026-27: 0.5512%; 2027-28: 0.3838%; 2028-29: 0.3081%
WLN - Willetton | 2024-25: 0.4531%; 2025-26: 0.6333%; 2026-27: 0.6679%; 2027-28: 0.9971%; 2028-29: 0.8872%
WNO - Wanneroo | 2024-25: 1.378%; 2025-26: 1.476%; 2026-27: 1.522%; 2027-28: 1.743%; 2028-29: 1.898%
WUN - Wundowie | 2024-25: 0.1942%; 2025-26: 0%; 2026-27: 0.2205%; 2027-28: 0.1951%; 2028-29: 0.2253%
Y - Yokine | 2024-25: 1.468%; 2025-26: 1.28%; 2026-27: 1.329%; 2027-28: 0.9028%; 2028-29: 1.066%
YER - Yerbillon | 2024-25: 0.04854%; 2025-26: 0.04308%; 2026-27: 0.07133%; 2027-28: 0.02059%; 2028-29: 0.00609%
YLN - Yilgarn | 2024-25: 0.2497%; 2025-26: 0.2434%; 2026-27: 0.2767%; 2027-28: 0.1994%; 2028-29: 0.205%
YP - Yanchep | 2024-25: 1.142%; 2025-26: 1.219%; 2026-27: 1.282%; 2027-28: 1.317%; 2028-29: 1.852%
Total | 2024-25: 84.77%; 2025-26: 84.61%; 2026-27: 82.64%; 2027-28: 85.6%; 2028-29: 86.77%
Table 3 1. The forecast demand of the following Block Loads are provided in MW, up to 2 decimal places, as measured at their respective Connection Points. 2. Block loads with CMD < 10MW are listed here to avoid their CMDs being exceeded when scaling up | bar: 2024-25
Load | 2024-25: 2024-25 (MW); 2025-26: 2025-26 (MW); 2026-27: 2026-27 (MW); 2027-28: 2027-28 (MW); 2028-29: 2028-29 (MW) | diff
ABD - Block Load 1 | 2024-25: 3.4; 2025-26: 3.4; 2026-27: 3.92; 2027-28: 2.89; 2028-29: 2.89
AFM - Block Load 2 | 2024-25: 4.2; 2025-26: 3.8; 2026-27: 2.3363; 2027-28: 2.34; 2028-29: 3.39
APJ - Block Load 3 | 2024-25: 15.2; 2025-26: 20.5; 2026-27: 26.38; 2027-28: 26.38; 2028-29: 26.38
BDE - Block Load 4 | 2024-25: 0.6; 2025-26: 0.6; 2026-27: 0.56974; 2027-28: 0.57; 2028-29: 0.96
BDP - Block Load 5 | 2024-25: 35.3; 2025-26: 41; 2026-27: 14.06; 2027-28: 14.16; 2028-29: 17.04
BEC - Block Load 6 | 2024-25: 9; 2025-26: 9.5; 2026-27: 0; 2027-28: 7.2; 2028-29: 7.2
BGM - Block Load 7 | 2024-25: 130.8; 2025-26: 130.1; 2026-27: 130.7371; 2027-28: 130.74; 2028-29: 125.93
BHK - Block Load 8 | 2024-25: 13.3; 2025-26: 3.7; 2026-27: 3.5597; 2027-28: 3.56; 2028-29: 3.72
BLV - Block Load 9 | 2024-25: 5.4; 2025-26: 5.4; 2026-27: 4.32; 2027-28: 4.32; 2028-29: 4.32
BNY - Block Load 10 | 2024-25: 9.5; 2025-26: 9.5; 2026-27: 6.719; 2027-28: 5.68; 2028-29: 7.33
BNY - Block Load 10a | 2027-28: 2.1; 2028-29: 2.24
BSI - Block Load 11 | 2024-25: 73; 2025-26: 72.4; 2026-27: 72.6186; 2027-28: 72.5; 2028-29: 72.5
CAR - Block Load 12 | 2024-25: 8.5; 2025-26: 8.1; 2026-27: 8.1; 2027-28: 7.9; 2028-29: 8.06
CBP - Block Load 13 | 2024-25: 9; 2025-26: 5.8; 2026-27: 7.72; 2027-28: 7.72; 2028-29: 2.57
CCL - Block Load 14 | 2024-25: 9.2; 2025-26: 10.6; 2026-27: 10.7498; 2027-28: 10.75; 2028-29: 8.35
CTB - Block Load 15 | 2024-25: 8.4; 2025-26: 8.2; 2026-27: 7.9; 2027-28: 11; 2028-29: 10.56
EDG - Block Load 16 | 2024-25: 7.1; 2025-26: 10; 2026-27: 11.48; 2027-28: 7; 2028-29: 7
FFD - Block Load 17 | 2024-25: 5; 2025-26: 5; 2026-27: 4; 2027-28: 5.02; 2028-29: 5.02
GGV - Block Load 18 | 2024-25: 17.2; 2025-26: 18.5; 2026-27: 21.1581; 2027-28: 21.16; 2028-29: 22.16
GNI - Block Load 19 | 2024-25: 13.2; 2025-26: 8.8; 2026-27: 8.8; 2027-28: 17.1; 2028-29: 9.1
KDP - Block Load 20 | 2024-25: 24.4; 2025-26: 21.5; 2026-27: 14.7292; 2027-28: 14.73; 2028-29: 11.53
KMC - Block Load 21 | 2024-25: 11.1; 2025-26: 9.4; 2026-27: 10.122; 2027-28: 10.12; 2028-29: 8.75
KMM - Block Load 22 | 2024-25: 9.1; 2025-26: 9.4; 2026-27: 7.7198; 2027-28: 7.72; 2028-29: 8.01
KRA - Block Load 23 | 2024-25: 78.7; 2025-26: 111; 2026-27: 69.6; 2027-28: 69.6; 2028-29: 72.8
MRN - Block Load 24 | 2024-25: 29; 2025-26: 27; 2026-27: 27; 2027-28: 1; 2028-29: 1.1
NOW - Block Load 25 | 2024-25: 7.5; 2025-26: 6.8; 2026-27: 4.7; 2027-28: 6; 2028-29: 7.6
NP - Block Load 26 | 2024-25: 8.1; 2025-26: 11.7; 2026-27: 4.7; 2027-28: 6; 2028-29: 9.98
PLD - Block Load 27 | 2024-25: 4; 2025-26: 6.2; 2026-27: 6.2; 2027-28: 11.56; 2028-29: 6
SUM - Block Load 28 | 2024-25: 8; 2025-26: 10.1; 2026-27: 8.0584; 2027-28: 8.06; 2028-29: 7.5
TLA - Block Load 29 | 2024-25: 16; 2025-26: 2.5; 2026-27: 4.41; 2027-28: 4.41; 2028-29: 5.15
TPP - Block Load 30 | 2024-25: 27.8; 2025-26: 21.8; 2026-27: 16.3036; 2027-28: 16.3; 2028-29: 16.3
WCL - Block Load 31 | 2024-25: 5.5; 2025-26: 4.3; 2026-27: 4.2027; 2027-28: 4.2; 2028-29: 3.86
WM - Block Load 32 | 2024-25: 31.3; 2025-26: 30.9; 2026-27: 15.9938; 2027-28: 16; 2028-29: 13.93
WSD - Block Load 33 | 2024-25: 5.9; 2025-26: 18.7; 2026-27: 2.1; 2027-28: 2.1; 2028-29: 11.17
AKW - Block Load 34 | 2024-25: 0; 2025-26: 2.7; 2026-27: 1.54; 2027-28: 1.54; 2028-29: 1.54
WAPL - Block Load 35 | 2024-25: 0; 2025-26: 4.4; 2026-27: 0; 2027-28: 0; 2028-29: 0
WHT - Block Load 36 | 2024-25: 10; 2025-26: 10; 2026-27: 8; 2027-28: 8; 2028-29: 8
SCE - Block Load 37 | 2024-25: 0; 2025-26: 0; 2026-27: 0; 2027-28: 0; 2028-29: 0
BTN - Block Load 38 | 2024-25: 15; 2025-26: 30; 2026-27: 36; 2027-28: 36; 2028-29: 36
MRR(523) - Block Load 39A | 2024-25: combined with other loads; 2026-27: 16.4; 2027-28: 16.42; 2028-29: 16.05
MRR(526) - Block Load 39B* | 2026-27: 7.56; 2027-28: 7.99; 2028-29: 1.24
MRR (512 & 531)- Block Load 40 | 2026-27: 5; 2027-28: 5; 2028-29: 5
PKS - Block Load 41 | 2024-25: 0; 2025-26: 0; 2026-27: 0; 2027-28: 0; 2028-29: 0
YP - Block Load 42* | 2026-27: 27.12; 2027-28: 27.12; 2028-29: 27.12
BNL - Block Load 43* | 2026-27: 7.5; 2027-28: 6; 2028-29: 9.8
BPR - Block Load 44 | 2027-28: 3.68; 2028-29: 3.94
BCH - Block Load 45 | 2027-28: 4.32; 2028-29: 4.32
CK - Block Load 46 | 2027-28: 6; 2028-29: 6
WKT - Block Load 47 | 2027-28: 0.72; 2028-29: 4.1
OFE - Block Load 49 | 2027-28: 0; 2028-29: 6.28
LTH - Block Load 50 | 2027-28: 0; 2028-29: 0
Sub Total | 2024-25: 668.7; 2025-26: 713.3; 2026-27: 650.0879; 2027-28: 660.68; 2028-29: 659.79
* Recently committed loads.